## Register
Asset tag | Gearbox | Casting batch | Substation | Last service | Vibration mm/s RMS | Status | Technician | Work order | Vendor
WTG_A17 | GBX_A17_02 | GBX_BATCH_2023_11 | SUB_NORD_02 | 2025-11-04 | 5.9 | failed | Anders Bjerg | WO_88231 | Halvard Drivetrain
WTG_A18 | GBX_A18_01 | GBX_BATCH_2023_11 | SUB_NORD_02 | 2025-11-06 | 3.8 | warning | Anders Bjerg | WO_88236 | Halvard Drivetrain
WTG_A03 | GBX_A03_02 | GBX_BATCH_2023_05 | SUB_NORD_01 | 2025-10-02 | 2.6 | normal | Tomas Novak | WO_88147 | Halvard Drivetrain
WTG_A06 | GBX_A06_01 | GBX_BATCH_2022_04 | SUB_NORD_01 | 2025-11-11 | 1.6 | normal | Lars Jorgensen | WO_88203 | Halvard Drivetrain
WTG_A07 | GBX_A07_01 | GBX_BATCH_2024_03 | SUB_NORD_01 | 2026-01-08 | 1.3 | normal | Mette Sorensen | WO_88298 | Halvard Drivetrain
WTG_A10 | GBX_A10_01 | GBX_BATCH_2022_04 | SUB_NORD_02 | 2025-11-14 | 1.7 | normal | Lars Jorgensen | WO_88209 | Halvard Drivetrain
WTG_A14 | GBX_A14_01 | GBX_BATCH_2024_03 | SUB_NORD_02 | 2026-01-19 | 1.5 | normal | Mette Sorensen | WO_88312 | Halvard Drivetrain
WTG_A16 | GBX_A16_01 | GBX_BATCH_2023_05 | SUB_NORD_02 | 2025-10-21 | 2.3 | normal | Tomas Novak | WO_88178 | Halvard Drivetrain
WTG_B04 | GBX_B04_01 | GBX_BATCH_2022_04 | SUB_HORNS_01 | 2026-01-19 | 1.6 | normal | Mette Sorensen | WO_88316 | Brantvik Gear Systems
WTG_B05 | GBX_B05_01 | GBX_BATCH_2024_03 | SUB_HORNS_01 | 2026-02-04 | 1.2 | normal | Mette Sorensen | WO_88341 | Brantvik Gear Systems
WTG_B08 | GBX_B08_01 | GBX_BATCH_2024_03 | SUB_HORNS_01 | 2026-02-09 | 1.4 | normal | Mette Sorensen | WO_88349 | Brantvik Gear Systems

## Notes
Northwind Energy gearbox maintenance register, extract of recently serviced units.
Site: Esbjerg Nord and Horns Vest, the Danish North Sea. Grid connection GRID_DK1.
Vibration readings are broadband velocity at the high speed stage, measured under the method in standard NW_STD_0417 (Rev. 4).
The alarm limit is 4.5 mm/s RMS and the warning level is 3.2 mm/s RMS.
Gearboxes are supplied by Halvard Drivetrain and Brantvik Gear Systems. Strip down inspections are witnessed by the supplier.
This extract lists recently serviced units only. It is NOT a complete asset register and it is NOT a complete record of casting batch membership; query the asset register for those.
Extract approved by Priya Raman, lead reliability engineer, on 20 March 2026.